LaminaHeat

PowerBoard

INSTALLATION GUIDE

PBS-750/500W Standalone Panel  |  PBS-250W Ceiling System

| Document Reference LH-PB-IG-EN-001 | Version 1.0 — 2025 |
| --- | --- |
| Applicable Products PBS-750W PBS-500W· PBS-250W | Contact info@laminaheat.com |

LaminaHeat Holding  ·

Tel: +49 6352 7199760  ·  info@laminaheat.com  ·  www.laminaheat.com

1. Introduction & Product Overview

LaminaHeat PowerBoard panels are advanced far-infrared radiant heating panels designed for ceiling-mounted installation. The heating element uses a full-surface carbon fibre heating film developed by LaminaHeat, giving each panel a profile equivalent to standard 600 mm × 1200 mm plasterboard. PowerBoard panels deliver comfortable, low-cost radiant heat with an in-room thermal efficiency exceeding 92%.

Once energised, the panel surface reaches its target temperature within approximately 8 minutes, bringing a room to a warm and comfortable state within 10–20 minutes. Because heat is delivered primarily through far-infrared radiation, the warmth is rapid, even, and energy-efficient — warming people and objects directly rather than circulating air.

NOTE: This guide covers two distinct product types with different installation methods. Read the product-specific sections carefully before beginning work.

1.1 Product Differentiation

| SPECIFICATION | PBS-750W | PBS-500W | PBS-250W |
| --- | --- | --- | --- |
| Product Model | PBS-750W | PBS-500W | PBS-250W |
| Rated Output | 750 W ± 10% | 500 W ± 10% | 250 W ± 10% |
| Heat Output (W/m²) | 1,480 ± 10% | 980 ± 10% | 480 ± 10% |
| Panel Length | 1,200 mm | 1,200 mm | 1,200 mm |
| Panel Width | 600 mm | 600 mm | 600 mm |
| Heating Width (active zone) | 470 mm | 470 mm | 470 mm |
| Panel Thickness | 12 mm | 12 mm | 12 mm |
| Current Draw per Panel | 3.33 A ± 10% | 2.08 A ± 10% | 1.04 A ± 10% |
| Supply Voltage | 230–240 V AC, 50 Hz | 230–240 V AC, 50 Hz | 230–240 V AC, 50 Hz |
| Resistance per Panel | 72 Ω +/-10% | 115 Ω +/-10% | 230 Ω +/-10% |
| Panel Weight | 10 kg (approx.) | 10 kg (approx.) | 6.6 kg (approx.) |
| Max. Panels per 16A Circuit | 4 panels | 8 panels | 14 panels |
| Installation Method | Surface-mount (exposed) OR ceiling joist/batten | Surface-mount (exposed) OR ceiling joist/batten | Ceiling joist/batten ONLY — integrated into plasterboard ceiling |
| Suitable for Exposed Mounting | YES — purpose-designed bracket | YES — purpose-designed bracket | NO |
| Suitable for Concealed Ceiling | YES | YES | YES |

1.2 Key Differences at a Glance

Understanding the distinction between these two products is essential before planning any installation:

| PBS-750W — Standalone Panel - High-output single panel (750 W) - Can be installed as an exposed surface-mounted panel using the supplied bracket — visible on the ceiling - Reaches 100-110C surface temp - Two-part assembly: fixing bracket + panel body - Max 4 panels per 16A circuit | PBS-250W — Ceiling System Panel - Lower-output panel optimised for multi-panel ceiling systems - Concealed ceiling installation ONLY — designed to sit flush within a standard suspended plasterboard ceiling - Cannot be surface-mounted — no exposed bracket available - Screws directly to ceiling joists/battens using pre-drilled holes - Max 14 panels per 16A circuit — ideal for whole-room systems |
| --- | --- |
| PBS-500W — Standalone Panel - High-output single panel (500 W) - Can be installed as an exposed surface-mounted panel using the supplied bracket — visible on the ceiling - Reaches 75-85C surface temp - Two-part assembly: fixing bracket + panel body - Max 8 panels per 16A circuit |

2. Safety Requirements

WARNING: Read this entire section before commencing any installation work. Failure to comply with these requirements may result in death, serious injury, fire, or voiding of the product warranty.

2.1 Mandatory Safety Warnings

WARNING: All electrical installation work MUST be carried out by a qualified and Part P-competent electrician (England & Wales), a SELECT-registered electrician (Scotland), or an NICEIC/NAPIT-registered contractor. Installation must comply with BS 7671: Requirements for Electrical Installations (IET Wiring Regulations, 18th Edition) and any applicable local building regulations.

- A Residual Current Device (RCD) with a maximum trip current of 30 mA MUST be installed on all circuits supplying PowerBoard panels. This is a mandatory requirement under BS 7671 Chapter 41.

- An Earth Fault Protection Device (EFPD) must be fitted in accordance with BS 7671.

- The supply circuit MUST be isolated and proven dead (using an approved voltage indicator) before any connection, fixing, or wiring work is carried out.

- PowerBoard panels operate at 230–240 V AC. Do NOT touch any electrical connections with wet hands or while standing on wet surfaces.

- ELECTRIC SHOCK HAZARD: Do not drive nails, screws, or any sharp objects through a PowerBoard panel. The carbon fibre heating film is an energised component.

- Minimum ceiling height for installation is 1.8 m. Do not install in spaces below this height.

- Do not install in rooms containing swimming pools, hot tubs, or similar wet areas unless a specific IP-rated variant is specified for such locations.

- Do not install where the supply voltage exceeds 240 V AC. Use with voltages above this threshold will void the warranty and may cause damage or fire.

- Do not cut, pierce, modify, or overlap panels in any way. Modification changes the electrical characteristics of the heating element and will cause overheating or fire.

2.2 Fire & Thermal Safety

- All insulation materials in contact with or adjacent to PowerBoard panels must have a minimum fire rating of Class B-s1,d0 in accordance with EN 13501-1 (equivalent to Class 1 surface spread of flame under BS 476). In practice, use non-combustible insulation such as mineral wool, glass wool, or Class A2 rigid foam.

- Do not cover a PowerBoard panel with any thermally insulating material (blankets, rugs, or similar) that would prevent normal heat dissipation. Doing so will cause overheating.

- If a burning smell, discolouration on the panel surface, abnormal indicator light colour, or audible buzzing from the controller is detected, isolate the circuit immediately and contact LaminaHeat or a qualified service engineer.

- Panels must not be installed directly over or below combustible stored materials.

2.3 Compliance Standards

This product and its installation must comply with the following standards and regulations:

| Standard / Regulation | Description | Applicability |
| --- | --- | --- |
| BS 7671:2018+A2:2022 | IET Wiring Regulations 18th Edition | All UK electrical installations |
| Part P, Building Regulations | Electrical safety in dwellings (England & Wales) | Residential installations |
| BS 8000-1 | Workmanship on building sites — Code of practice for excavation and filling | Site practices |
| EN 60335-2-96 | Safety of heating pads and electric heating films | Product electrical safety |
| EN 13501-1 | Fire classification of construction products | Insulation fire rating |
| BS EN ISO 9001 | Quality management systems | Installer qualifications |
| CDM Regulations 2015 | Construction Design & Management | Commercial/notifiable projects |

3. Pre-Installation Planning

3.1 Tools & Materials Checklist

Ensure all the following are available before beginning installation:

| Tools - Tape measure (3 m+) - Spirit level - Cordless drill / driver - Pencil / chalk line - Voltage indicator (approved) - Torque screwdriver - Cable stripper / crimping tool - PPE: safety glasses, gloves | Materials - PowerBoard panels (PBS-750/500W or PBS-250W) - 38 mm plasterboard screws (PBS-250W) - Appropriate rawl plugs / expansion anchors (PBS-800W to concrete) - Thermostat(s) — 16A rated minimum - Appropriately rated cable (see Section 5) - Consumer unit / fuse board with RCD protection - Junction boxes / wiring accessories - Suitable mineral wool or Class A2 insulation (if required) |
| --- | --- |

3.2 Calculating Room Heat Load

Before determining the number of panels required, calculate the room's heat load (heating demand) using the following method:

| Building Type | Heat Demand Index (W/m²) | Notes |
| --- | --- | --- |
| Well-insulated new-build / Passivhaus | 40–60 W/m² | Excellent fabric insulation, MVHR ventilation |
| Modern cavity-insulated dwelling | 60–80 W/m² | Meets current Part L requirements |
| Older property with some insulation | 80–100 W/m² | Partial wall/loft insulation |
| Older property, limited insulation | 100–130 W/m² | Solid brick or stone walls, minimal insulation |
| Self-build, no external insulation | 130–150 W/m² | Bare construction, no insulation |

Ceiling Height Correction Factor: The values above assume a ceiling height of 2.5 m or less. If ceiling height exceeds 2.5 m, apply the following correction:

Adjusted Heat Load Formula (ceiling height 2.5–3.5 m): Adjusted Heat Load = Base Heat Load × [1 + 0.3 × (Actual Height − 2.5)] Example: 30 m² room, modern cavity-insulated dwelling (80 W/m²), 2.8 m ceiling: Adjusted Load = 80 × 30 × [1 + 0.3 × (2.8 − 2.5)] = 2,400 × 1.09 = 2,616 W Number of PBS-250W panels required = 2,616 ÷ 250 = 10.5 → round UP to 11 panels

CAUTION: Do not install PowerBoard panels in rooms with ceiling heights exceeding 3.5 m without first consulting LaminaHeat or a qualified heating engineer. At heights above 3.5 m, radiant heating efficiency falls significantly and alternative strategies may be required.

3.3 Insulation Best Practice

PowerBoard infrared panels are most efficient in well-insulated spaces. While panels can be installed in any room, the following insulation standards should be targeted to maximise comfort and minimise running costs:

- Loft/roof insulation: minimum 270 mm mineral wool to comply with current Building Regulations Part L.

- External wall insulation: cavity-fill or solid-wall insulation to achieve a U-value of 0.30 W/m²K or better.

- Floor insulation: 100 mm rigid foam insulation beneath the ground floor where possible.

- Windows: double or triple-glazed units with a U-value of 1.6 W/m²K or better.

- At minimum, install insulation directly above the ceiling void where panels are located to prevent heat loss through the ceiling structure.

- Use only insulation materials with a thermal conductivity (lambda value) of 0.040 W/mK or lower. Do not use insulation that emits harmful volatile compounds or supports microbial growth.

BEST PRACTICE: LaminaHeat strongly recommends a whole-house insulation survey before installation. Contact LaminaHeat or an approved installer for a heat-loss assessment to ensure correct panel sizing.

4. Panel Layout & Positioning

4.1 General Layout Principles

Correct panel layout is critical for achieving uniform room heating. Follow these principles for both product types:

- Distribute panels as evenly as possible across the ceiling area to ensure uniform heat coverage.

- Place the FIRST row of panels approximately 600 mm horizontally from any external wall or external window. This counteracts the higher heat loss at the building perimeter and improves occupant comfort.

- Do NOT position panels directly opposite a large window. Infrared radiation will pass straight through the glazing, wasting energy.

- Concentrate panels near areas of higher heat loss (external walls, north-facing walls, large windows) while keeping minimum spacing from each other.

- Adjacent panels must have a minimum edge-to-edge gap of 10 mm. Do not allow panels to touch or overlap.

- Ensure all power cables route upward through the ceiling structure away from the panel face.

4.2 Recommended Layout by Heat Demand Index

The following panel density guidelines apply to PBS-250W ceiling installations. Adjust proportionally for PBS-750/500W panels:

| Heat Demand Index | PBS-250W Panel Density | Typical Applications |
| --- | --- | --- |
| 40 W/m² | 1 panel per 6.25 m² ceiling | Passivhaus, well-insulated extension |
| 60 W/m² | 1 panel per 4.2 m² ceiling | Modern new-build |
| 80 W/m² | 1 panel per 3.1 m² ceiling | Standard cavity-insulated home |
| 100 W/m² | 1 panel per 2.5 m² ceiling | Older property with some insulation |
| 130 W/m² | 1 panel per 1.9 m² ceiling | Poor insulation / high heat loss |

BEST PRACTICE: Always round the number of panels UP to the next whole number. Slightly oversizing the system improves comfort and reduces the duty cycle of each panel, extending its service life.

4.3 Layout Restrictions

- Maintain a minimum clearance of 50 mm between panel edges and recessed light fittings.

- Do not install panels directly above structural beams if doing so would prevent adequate fixing or create a gap greater than 20 mm between the panel and the ceiling plane.

- Mark out the intended panel positions in pencil on the ceiling structure before beginning installation to verify spacing and cable routing.

- For PBS-250W: confirm joist/batten centres align with the panel's pre-drilled fixing holes before marking out.

5. PBS-250W Installation — Ceiling System

CAUTION: The PBS-250W is designed exclusively for concealed installation within a suspended plasterboard ceiling. It CANNOT be surface-mounted. This section assumes installation into a standard metal-frame or timber-joist suspended ceiling system.

5.1 Ceiling Structure Requirements

- The ceiling structure must be capable of supporting the panel weight (6.6 kg per panel) plus the weight of overlying plasterboard and insulation.

- For metal stud/batten ceilings: battens must be spaced at 600 mm centres (matching the 600 mm panel width) with minimum 47 × 47 mm metal section.

- For timber-joist ceilings: joists must be at 600 mm centres or blocking/noggins must be installed to provide fixing points for the panel edges.

- The finished ceiling height must be a minimum of 1.8 m above floor level.

5.2 Step-by-Step Installation Procedure

Important: All electrical cable routing should be completed and cables positioned prior to panel installation. Do not energise the circuit during mechanical installation.

- Begin in the corner of the room closest to the external wall or external window. Position the first panel 600 mm horizontally from the wall/window.

- Orient the panel so its LONG EDGE runs perpendicular to the ceiling joists/battens. The power cable tail should extend upward toward the ceiling void.

- Before fixing, verify the panel is level using a spirit level. If the ceiling structure is uneven, pack as required to achieve a level installation.

- Using 38 mm plasterboard screws, fix the panel through its pre-drilled holes into the ceiling joists or battens. Use all provided fixing holes.

- The screw head should sit flush with the panel surface — do not over-drive screws as this will deform the panel face.

- Maintain a minimum 10 mm gap between adjacent panel edges.

- Once all panels in a zone are fixed, route power cables through the ceiling void. Cables must be enclosed in appropriate conduit or clipped to joists as required by BS 7671.

- Once panels and wiring are complete, install plasterboard adjacent to the panels to complete the ceiling. Skim or tape-and-joint to achieve a flush finish.

- Do not apply the final plasterboard skim coat, paint, or decorative finish until the system has been energised, inspected, and confirmed operational. The panel surface should be fully dry before commissioning.

WARNING: Do not energise the system until all jointing compound and skim coats have FULLY DRIED. The rapid temperature rise of the panel surface may cause wet plaster or jointing compound to crack.

5.3 Finishing

- PowerBoard panels are designed to sit flush within the ceiling plane. Once adjacent plasterboard is installed, apply jointing tape and joint compound to the panel edges to create a seamless finish.

- Standard emulsion paint (minimum 10-year rated) may be applied over the panel face once the surface is confirmed dry and the system has completed its first commissioning run.

- Do not apply tiles, heavy plaster coats, or thermally insulating decorative materials to the panel face.

6. PBS-750/500W Installation — Standalone Panel

NOTE: The PBS-750/500W can be installed in two configurations: (A) exposed surface-mount using the supplied fixing bracket, or (B) flush in a standard profile ceiling. Read the appropriate sub-section for your installation type.

6.1 Configuration A: Exposed Surface-Mount

This configuration is suitable where a suspended ceiling is not planned or where a visible radiant panel is acceptable. The panel is mounted directly to the ceiling surface using the two-part bracket system.

6.1.1 Bracket Installation — Concrete / Masonry Ceiling

- Mark fixing hole positions on the ceiling, ensuring the bracket is positioned to accept the panel in the correct orientation (long axis perpendicular to any external wall).

- Drill holes at the marked positions using an appropriate SDS drill bit. Insert M6 expansion anchors (rawl plugs) rated for a minimum pull-out load of 150 N per fixing.

- Verify that all cable routes and conduit have been installed BEFORE attaching the bracket, as access will be restricted once the bracket is fixed.

- Secure the fixing bracket to the ceiling using M6 bolts. Torque fixings to the bracket manufacturer's specification. Verify the bracket is level before full tightening.

6.1.2 Bracket Installation — Timber Joist / Batten Ceiling

- Position the bracket over the ceiling joists or battens. The bracket fixing holes must align with solid timber — do not fix into plasterboard only.

- Use 50 mm timber screws (minimum No. 10 gauge) through the bracket holes into solid joists.

- Verify the bracket is level and secure before proceeding.

6.1.3 Attaching the Panel Body

- Route the panel power cable tail upward through the bracket opening before clipping the panel body into place.

- Align the panel body with the bracket and engage the clip fasteners — you should feel a positive click as each fastener engages.

- Gently tug the panel to confirm it is fully secured before making any electrical connections.

- A minimum clearance of 50 mm must be maintained between the panel face and any adjacent surface, fitting, or object.

CAUTION: Because the PBS-750/500W surface operates at elevated temperatures in this exposed configuration, ensure that no curtains, furniture, or flammable materials are positioned within 300 mm of the panel face.

6.2 Configuration B: Concealed Ceiling Installation

When installing the PBS-750/500W within a suspended plasterboard ceiling, the procedure is identical to the PBS-250W installation (Section 5), with the following differences:

- The ceiling structure must be rated to support 10 kg per panel (the PBS-750/500W is heavier than the PBS-250W). Verify joist or batten load capacity accordingly.

- The two-part bracket is used: first fix the bracket to the joist/batten, then clip the panel body onto the bracket from below.

- Ensure all cable routing is completed before the panel body is clipped onto the bracket, as access to the ceiling void will be restricted after panel installation.

- Maximum 4 × PBS-750W or 8x500W panels per 16A circuit. Do not exceed this limit under any circumstances.

7. Electrical Connections

WARNING: All electrical connection work MUST be performed by a qualified, registered electrician. All circuits must be isolated and proved dead before work commences. The installation must comply with BS 7671:2018+A2:2022 (18th Edition IET Wiring Regulations) and be notified to Building Control where required under Part P.

7.1 General Wiring Principles

- All panels must be connected in PARALLEL to a common bus. Do not wire panels in series.

- The common bus connects to the thermostat, which in turn connects to the supply. The thermostat controls the heating zone by switching all panels simultaneously.

- Install one thermostat per room or heating zone. The thermostat must be located in the same room as the panels it controls to enable accurate ambient temperature sensing.

- Use a minimum 2.5 mm² twin and earth cable (T&E) for all circuit wiring. For runs exceeding 20 m, consider upgrading to 4 mm² to limit voltage drop below 3% as required by BS 7671 Regulation 525.

- Each panel comes with a quick-connect plug-and-socket system. This significantly simplifies installation and reduces connection errors.

- Label all cables at both ends before pulling through conduit or ceiling voids. Use permanent cable markers.

7.2 Circuit Sizing

| Configuration | Max Panels | Total Load |
| --- | --- | --- |
| PBS-250W only (no contactor) | Up to 14 panels | Up to 3,500 W / 15.2 A |
| PBS-500W only (no contactor) | Up to 8 panels | Up to 4000, W / 16 A |
| PBS-750W only (no contactor) | Up to 4 panels | Up to 3,200 W / 13.9 A |
| Mixed or higher load (with contactor) | As designed | As calculated |

7.3 Contactor Wiring (Loads Above 16A)

Where the total connected panel load for a zone exceeds 3,500 W (approximately 15.2 A on a 230 V supply), a contactor must be installed between the thermostat and the panel circuit. The thermostat switches the contactor coil (low current) and the contactor switches the heating load (high current).

- Select a contactor rated for a minimum of 125% of the total connected load (e.g., 25A contactor for a 20A load).

- The contactor must be suitable for resistive AC1 load switching.

- House the contactor in an appropriate IP-rated enclosure within the ceiling void or at the distribution board.

- All contactor wiring must be enclosed in conduit or trunking and comply with BS 7671.

7.4 Thermostat Installation

- The thermostat must be rated for a minimum of 16A switching capacity, or for the full load of the zone where no contactor is used.

- Mount the thermostat on an internal wall, 1.2–1.5 m above floor level, away from direct sunlight and draughts.

- Do not mount the thermostat on or directly adjacent to an external wall — this will result in inaccurate room temperature sensing.

- The LaminaHeat BHT-series WiFi thermostats are compatible with all PowerBoard products and are recommended for optimal control and energy monitoring.

BEST PRACTICE: For installations in commercial or public buildings (schools, care homes, offices), separate metering of the heating circuit is strongly recommended to enable energy monitoring and compliance with ESOS (Energy Savings Opportunity Scheme) or DECs (Display Energy Certificates) where applicable.

7.5 Zoning Best Practice

For whole-building or multi-room installations, the following zoning approach is strongly recommended:

- Install a separate, independently controlled circuit for each room or heating zone. This enables rooms to be heated only when occupied, significantly reducing energy consumption.

- Where smart thermostats are used (LaminaHeat BHT WiFi series), group zones by occupancy pattern (e.g., bedrooms on a nighttime schedule, living areas on a daytime schedule).

- A fault in one zone (tripped breaker, blown fuse) will not affect other zones if they are independently circuited.

- Label each circuit clearly at the consumer unit / fuse board with the room name and panel count.

8. Commissioning & Handover

8.1 Pre-Energisation Checks

Before energising the system, the installing electrician must confirm the following:

- All panels are mechanically secure and level.

- All electrical connections are completed, insulation resistance (IR) tested at 500 V DC, and results recorded (minimum acceptable: 1 MΩ).

- Earth continuity has been verified for all circuits.

- RCD trip times have been tested and verified (maximum 40 ms at 1× rated trip current).

- All plasterboard jointing compound and skim coats are FULLY DRY.

- All thermostats are correctly positioned and wired.

- Consumer unit / fuse board labelling is complete.

8.2 First Power-On

- Energise one circuit at a time. Set the thermostat to a temperature 3–5°C above the current room temperature.

- The panel surface temperature will reach its operating setpoint within approximately 8 minutes. Verify this using a non-contact infrared thermometer.

- The room will reach a comfortable temperature within 10–20 minutes of first power-on.

- During the first commissioning run, check all panels for any unusual sounds, smells, or visual anomalies. If any are detected, immediately isolate the circuit and investigate before proceeding.

- Allow the system to run for a minimum of 30 minutes during commissioning to verify stable operation.

BEST PRACTICE: Note for the occupant: Because infrared radiant heating warms people and objects (rather than the air), the recommended thermostat setpoint for infrared heating is typically 1–2°C lower than you would use with a conventional convective or wet heating system, while achieving the same perceived comfort level.

8.3 Commissioning Record

Upon completion, the installing electrician must provide the building owner with the following documentation:

- Completed Electrical Installation Certificate (EIC) or Minor Electrical Installation Works Certificate (MEIWC) as appropriate under BS 7671.

- Inspection and test schedule including IR test results, RCD test results, and earth loop impedance readings.

- Schedule of installed panels (product model, quantity, location, circuit reference).

- Thermostat manufacturer operating instructions.

- Completed LaminaHeat warranty registration (see Section 9).

9. Warranty Policy

LaminaHeat GmbH ("the Manufacturer") warrants that PowerBoard panels are free from defects in materials and workmanship under normal use conditions. The limited warranty period is 10 years from the date of installation by a LaminaHeat-approved installer. This warranty applies to the original owner of the installed product.

9.1 Making a Warranty Claim

- Notify the Manufacturer of a warranty claim within the limited warranty period, providing proof of purchase, installation records, and a description of the defect.

- The Manufacturer will inspect and test the product. If the defect is confirmed as a manufacturing fault occurring during normal use and correctly installed, the Manufacturer will provide a remedy free of charge.

- The remedy is limited to: repair of the product, replacement of the product, or a refund at the original purchase price.

- If a defect occurs within the 10-year limited warranty period, LaminaHeat will also contribute towards reasonable reinstallation costs. The level of contribution is determined on a case-by-case basis.

9.2 Warranty Exclusions

The warranty does not cover defects or failures resulting from any of the following:

- Improper or non-compliant installation.

- Cutting, piercing, modification, or physical damage to the panel at the installation site.

- Force majeure events including fire, flood, lightning, earthquake, or similar.

- Misuse, accident, abnormal vibration, or severe mechanical impact.

- Improper maintenance, cleaning, or storage.

- Operation at supply voltages outside the rated range (230–240 V AC).

- Installation by non-approved or unqualified personnel.

- Use of the product in applications for which it was not designed.

WARNING: Warranty is automatically voided if: the panel has been cut, modified, or overlapped; if installation was not performed by a qualified electrician; or if supply voltage exceeded 240 V AC.

9.3 Contact Information

|  | LaminaHeat — China Building 8, Unit 1902, Jinling Garden Area B Xianxia Ridge Road No. 12, Laoshan District Qingdao, Shandong, China Tel: +86 18678618385 Email: sduchene@laminaheat.com |
| --- | --- |

Appendix A: Quick Reference — PBS-750/800W vs PBS-250W

| Installation Step | PBS-750/500W | PBS-250W |
| --- | --- | --- |
| Ceiling height minimum | 1.8 m | 1.8 m |
| Ceiling height maximum (standard) | 3.5 m | 3.5 m |
| Mounting method | Bracket (surface) or joist/batten (concealed) | Joist/batten only (concealed) |
| Fixing hardware | M6 expansion anchors (concrete) / 50 mm timber screws (timber) | 38 mm plasterboard screws |
| Max panels per 16A circuit | 4/8 | 14 |
| Cable type (minimum) | 2.5 mm² T&E | 2.5 mm² T&E |
| RCD requirement | 30 mA, type A or AC | 30 mA, type A or AC |
| Earth continuity required | Yes | Yes |
| Thermostat rating (min.) | 16A | 16A |
| Contactor required (>16A load) | Yes, AC1 rated | Yes, AC1 rated |
| Min clearance from other panels | 10 mm edge-to-edge | 10 mm edge-to-edge |
| Min clearance from light fittings | 50 mm | 50 mm |
| Warranty period | 10 years (approved installer) | 10 years (approved installer) |

Appendix B: Regulatory Compliance Summary

The following table summarises the key regulatory requirements for PowerBoard installation in the United Kingdom:

| Requirement | Standard | Action Required |
| --- | --- | --- |
| Electrical installation | BS 7671:2018+A2:2022 | Qualified electrician, EIC on completion |
| Domestic notification | Part P, Building Regulations | Notify local authority or use Part P registered contractor |
| RCD protection | BS 7671 Reg. 411.3.3 | 30 mA RCD on all heating circuits |
| Earth fault protection | BS 7671 Ch. 41 | EFPD fitted |
| Voltage drop | BS 7671 Reg. 525 | Max 3% on final circuit |
| Cable sizing | BS 7671 App. 4 | Sized for continuous load + diversity |
| Fire safety of insulation | EN 13501-1 | Min. Class B-s1,d0 insulation adjacent to panels |
| Commercial projects | CDM Regulations 2015 | Principal Designer / Principal Contractor duties |
| Product safety | EN 60335-2-96 | Product supplied with CE/UKCA marking |

End of Document

LaminaHeat GmbH  ·  Morschheimer Str. 15  ·  67292 Kirchheimbolanden, Germany  ·  info@laminaheat.com